COMPUTER ROOM AC UNITS

## CLOSE CONTROL TWIN CIRCUIT RANGE

- The close control twin circuit air cooled range has 4 unit sizes providing nominal capacities of 30 - 100kW.

- Units are available in air and dual cooled versions.

- Units are available in upflow, downflow and downflow front discharge displacement airflow configurations.

- Standard DX units on R407C with an option on R410A.

- Condensers can be selected for 30, 35, 40, 45 & 50 ambients.

- Standard units have forward curved belt driven fans, with an option on backward curved direct drive EC fans.

- BMS interfaces available are MODBUS, BACnet, MSTP, BACnet IP, SNMP IP, LON & Trend.

- Full range of options available including:

  - Reheat of various types

  - Humidifiers

  - Electronic expansion valves

  - Discharge and acoustic plenums

  - Floorstands and dampers

  - Upgraded filter class

  - Fire and smoke detectors

  - Water detection

  - Condensate pumps

| Model |  | 30 | 40 | 50 | 60 | 70 | 80 | 100 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Air Volume | m3/hr | 8250 | 11000 | 13750 | 15500 | 18000 | 20500 | 25000 |
| Total Capacity - DX | kW | 30.6 | 42.8 | 47.8 | 64.4 | 69.8 | 81.8 | 108.6 |
| Sensible Capacity - DX | kW | 28.0 | 39.0 | 44.8 | 60.6 | 66.6 | 78.3 | 100.8 |
| Total Capacity - CW | kW | 32.9 | 40.9 | 52.3 | 57.1 | 70.7 | 77.8 | 94.7 |
| Sensible Capacity - CW | kW | 31.1 | 40.9 | 50.8 | 57.1 | 67.2 | 75.1 | 91.6 |
| Unit Length | mm | 1660 | 1660 | 2000 | 2000 | 2500 | 2500 | 2800 |

- Nominal Capacity based on 22°C & 50%RH return air, and for chilled water an entering temperature of 6°C.

- Unit measurements for depth and height are 875mm and 1980mm respectively.